Emergency Power Control (EPC)/ Automatic Load Control Relay (ALCR) Specification

1      Electrical Specifications

  - The EPC shall automatically illuminate connected emergency loads at full brightness upon utility power interruption, regardless of room switch position. (NEC 700.24)

  - Local room switch, dimmer, or lighting control shall control both normal  & emergency luminaires together (no dedicated emergency control required).

  - The EPC shall include a dry contact for 0-10V override during utility power interruption.

  - The EPC shall include an automatic diagnostic which is initiated when the room switch is turned off.  This test procedure will turn the emergency luminaires on for at least 2 seconds, indicating that an emergency power source is available & that the device, ballast, & lamp are all functioning correctly.

  - The automatic diagnostic feature shall be field-selectable through a jumper wire or dip switch.

  - Automatic diagnostic shall be approved to meet periodic testing requirements (NEC 700.3 NFPA 101 7.9.3).

  - The EPC shall include a fire alarm override input.

  - The EPC shall have a load rating of 20 Amps at 120V or 277V , 1800W Tungsten at 120V & 1500W Tungsten at 277V, 1 HP, General Use 20 Amps.

  - The EPC shall accept 120-277V 50-60 Hz Input & Output (voltage tolerance +/- 15%).

  - The EPC shall include emergency power and regular power indicator LED’s and a manual test switch which are visible to room occupants when installed flush. (UL924 Section 29)

  - The EPC shall be able to accept different phases on its constant & switched hot inputs.

  - The EPC shall include high voltage input surge protection up to 50,000V.

1.10 Load contacts shall be able to withstand 10 direct shorts while connected to 20 Amp breaker without permanent damage.

1.11 The EPC shall not generate any objectionable electrical or mechanical noise.

- Mechanical Specifications

  - The EPC shall mount inside a 4-11/16” junction box with an extension box & single gang plaster ring or blank cover.

  - The EPC shall include a decorative style flush adaptor plate and permit flush mounting so that test switch & LED’s are in plain view of room occupants as required by some local electrical codes.

  - The EPC shall include mounting feet for fixture or junction box mounting as alternative methods.

  - The EPC shall have UL94-V0 or UL94-5VA flame rating and be tested to UL2043 and approved for plenum installation.

  - Enclosure shall be white

  - Dimensions: Flush plate:  4-3/4” x 2-3/4” x 1/4” Recessed body: 2-7/8” x 1-3/4” x 1-3/4”

- General Specifications

3.1  The EPC shall be UL924 listed.

3.2  Warranty shall be 5 year replacement warranty

3.3  The EPC shall comply with all N.E.C., N.F.P.A, OSHA, & local safety codes.

Emergency Power Control shall be model EPC-2-D by LVS, Inc. 800-982-4587  www.lvscontrols.com